

          Lake Point Improvement District

7856 Mountain View Road

Lake Point, Utah 84074

Approved

Board Meeting Minutes

The Lake Point Improvement District held its regularly scheduled Business meeting on July 11, 2024 at 7:00 p.m. at the Broken Arrow Conference Room at 8960 Clinton Landing Road, Lake Point Utah.  The agenda is as follows:

1.
Call to Order


Chairman to call the meeting to come to order @:  7:16

Motion:  Brady

Seconded:  Todd

Roll Call:
Todd   Brady   Scott   Jared   Ryan

Treasurer:  Terre Marshall

Engineer:  AJ. 
Shaffer

Operator:  Keith Fryer   

 Guests:   None
2.
Public Concerns or Comments


None













3.
Approval of Minutes


Business Meetings – June 2024


Comments or corrections:   None


Approval of the minutes for the Business Meetings of June 2024



Motion Brady   Seconded:  Scott;   In Favor:  5;   Opposed;   0;   Motion Carries:   Yes
4.
Financial Reports –


A.
Approval of Bills – 2024



Comments:  Terre reviewed each check draft for approval




Corrections/comments: No corrections or adjustments




ACH Merchant processing fee


$   88.54




Impact Fee Checking, Funds Transfer

$250.00






Hayne and Company (Annual Audit)


$8000.00





Keith Fryer Expense (2 Months)


$5200.00



     .
Motion to approve; Checks 4588 - 4595 + ACH fees $187.37;   Total: $16,391.53




    Motion: Scott;   Seconded: Todd;   In Favor: 5;   Opposed: 0;   Motion Carries: Yes 


    B.
Budget Report – 2023




Total Income

 $ 151,391.21
       47.3% of budget        ($320,258.42)      



Total Expenses
 $   56,122.30         44.3% of budget        ($126,644.73)




Net ordinary income  
 $   95,268.91         49.2% of budget        ($193,613.69) 


     C.
Balance Report –2024



Rate Payer Checking:     48,383.40

Impact Fee Checking:     $ 17,255.79 



    
 LPID Rate Payer and Impact Fee checking accounts funds transfer authorization:  




     No transfer to PTIF; awaiting road repair invoice.





Impact Fee Checking: $ 0.00       Rate Payer Checking   $0.00

5.
Operations Reports


A.
UPDES Compliance Report






April

May

June

Limits



Influent BOD   = 
141

207

113

ppm




Influent TSS     = 
201

169

338

ppm



Effluent BOD   =   
43

27

26

(limit is 45ppm).




Effluent TSS     =   
78

31

46

(limit is 45 ppm) 




pH    

  =       
8.8

8.6

8.7

(limit >6.0<9.0)




Coliform:   
  =        <1

<1(

1

limit is 128)




Influent Flow    =     
0.517

0.643

0.511

mgd



Effluent Flow    =     
0.754

0.550

0.257

mgd



Effluent parameters were within permits except for effluent TSS at 46mgl. Aeration time 



is 4 hours/day for the month of June primarily for mixing in cell #1.  Cell #2 had a 



reduced algae bloom and Cell #3 was clear except for precipitated calcium carbonate. 



(White cloudiness, not green algae)



B.
Influent flow decreased from 0.643 mgd in May to 0.511 mgd in June. 


C.
The Canyon Road sewer pipeline was jet cleaned from the west manhole on Foothill 



Road to 720 feet going east on Canyon Road.  There are a number of elm trees along this 



sewer line and just to be sure the tree roots have not worked their way into the sewer pipe 


(all 4 foot concrete sections), it was cleaned.  No evidence of tree roots was found, just a 



small amount of sand.
6.
UPDES Permit Renewal



A.
The current UPDES Permit will expire on June 30, 2025.  LPID must apply for 




reissuance of a new permit not less than 180 days prior to the expiration date of the 



existing permit.  Application is in the process of being submitted.


B.
Monitoring effluent limitations expected to remain unchanged with the exceptions of 



percent removal for BOD, TSS and total residual chlorine.   BOD and TSS limitation 



could be a problem.  Percent removal was removed from past permits because of low 



influent TSS making it impossible to meet the percent removal. (Average influent equals 



250 and an effluent TSS of 31 = 88 %.; 300 mg/l X 0 .15 = 45mg/l
7.
Wastewater Lagoon Enhancement


Troy McKinley of Clear Water Innovations Company began injecting the live biological bacteria 

into the Regional Pump Station inlet on May 26, 2024. The mission is to enhance Lagoon based 


wastewater systems by working with native biology. The service based system provides simple 


work and cost effective solutions that work to improve quality and efficiency within current 


waster water treatment systems.  There is no cost to LPID for the test and all data collected on the 

performance of the innovation will be shared with the District.


Data to date shows some reduction in ammonia and phosphorus.  More data will be required 


before definite trends become evident.

8.
Civic Review Process



Lake Point City has instigated a new check off list for entities to sign off on certain required 


documents before the city can issue a building permit.  LPID must sign off on Plat approval.

9.
Colette and Rock Hollow Road Repair - Status


Work completed?


Staker and Parsons have been awarded the contract to make the road repairs in the Lake Point 


Area.  The work is scheduled for third week in July

0.
Plat 14 Roads



Plat 14 compaction tests have high failure rate (<95% compaction) for the roads being 



constructed in Plat 14.  The sewer trenches and water lines did not show any evidence of 



settlement when the heavy rains occurred in May.  The trenches to date not covered still show no 

signs of settlement.


The District's concern is when the roads are complete and moisture seeps into the road fill, it will 

settle and LPID will be blamed for the settlement of the road (as has been the case).



It may be in the best interest of LPID to have an attorney write a letter making note of the present 

compaction failures and any road failures due to settling not to be caused by settling of the sewer 

trenches, but to road failure due to improper compaction when the roads were constructed. 
11.
Quick Sump Update



1.
Facility to be opened in June


2.
A fact sheet was requested by LPID about Quick Sump




The specification of the filter media proved to be ineffective, plugged too soon.



3.
Pictures



4.
The solids seem to be the best filter media and the liquid portion filters down through the 



solids, only clear water drains into the final settling basin.


5.
The volume of water to drain is estimated to be 2 to 3 gallons per minute.



6.
A sample of the discharge water will be collected and analyzed for TSS, BOD, ammonia,




Phosphate and nitrate


7.
The number of truckloads being delivered is now averaging about one per day.




12.
Franchise Agreement - Status


LPID is still waiting a response from the Lake Point City Attorney 
13.
Sewer Easement Update


Update:  Ward Engineering continues to document the existing easements and will continue 


to search and record any new easements
14.
Temporary Sewer Service



The District needs to define a sewer connection to a travel trailer or similar temporary housing 


connected to a house with normal sewer service. The trailer in question is connected to a private 


water source (in contrast to the Oquirrh Trailer Park which the motel supplies water to the trailers 

serves as a means of charging the trailers for sewer service.) and the temporary service sewer 


lateral is connected to the owner's house nearby. The water consumption is expected to be less 


than an apartment because of no washing machines or other high water appliances. A basement 


apartment rental is charged the full monthly rate because of the water consumption similar to a 


regular house. An additional impact fee has not been charged for in house apartment rentals 


(because these rentals are considered temporary)


Commercial sewer service to a RV trailer dump should be considered in this resolution.



Holiday charges $5.00 for RV to empty their holding tanks into the sewer dump facility



Resolution:  2024-03.  



The charge for a sewer service for temporary connection to an existing 





house sewer system of mobile home type travel trailers ($10.41/month) or commercial 



trailer dump facilities shall be charged a monthly charge of $25.00 per-month). 


Motion:   Keith;   Seconded: Scott;   In Favor:  5;   Opposed:  0;  Motion  Carries: Yes 
15.
Other District Business & Trustee Concerns


A. 
Next LPID Meeting—August 8, 2024


B.
Other Trustee business: Brady



C.
Brady asked about GIS mapping of the Lake Point Area.  Some work is complete in other 



digital forms of mapping which may be converted to GIS format.
 16.
Adjournment


Motion to adjourn this meeting of the Lake Point Improvement District of July 13, 2024 @ 8:36 pm   


Motion:  Scott;   Seconded:  Todd;   In Favor:  5;  Opposed:  0;   Motion Carries  Yes
Minutes - July 2024
