

          Lake Point Improvement District

7856 Mountain View Road

Lake Point, Utah 84074

The Lake Point Improvement District held its regularly scheduled Business meeting on August 8, 2024 at 7:00 p.m. at the Broken Arrow Conference Room at 8960 Clinton Landing Road, Lake Point Utah.  The agenda is as follows:

1.
Call to Order


Chairman to call the meeting to come to order @:  7:04 pm

Motion:  Brady
Seconded:  Ryan

Roll Call:
Todd   Brady   Jared   Ryan; Scott absent

Treasurer:  Terre Marshall


Operator:  Keith Fryer    

Engineer:  A.J Shaffer


Guests:   None

2.
Public Concerns or Comments

None

3.
Approval of Minutes


Business Meetings – July 2024


Comments or corrections:   None



Approval of the minutes for the Business Meetings of July 2024



Motion Ryan;   Seconded;   Todd;   In Favor   4;   Opposed; 0   Carries   Yes
4.
Financial Reports –


A.
Approval of Bills – 2024



Comments:  Terre reviewed each check draft for approval




Corrections/comments:  None




ACH Merchant processing fee


$    58.79




Chemtech-Ford (Annual metals + 2 routine) 

 $1020.00





     .
Motion to approve; Checks 4596 - 4600 + ACH fees $58.79;   Total: $5861.63









    Motion: Todd;   Seconded:  Jared;   In Favor:  4;   Opposed:  0;   Motion Carries: Yes 


    B.
Budget Report – 2024



Total Income

 $ 168296.18         52.6 % of budget        ($320,258.42)      



Total Expenses
 $   61983.93         44.3% of budget          ($126,644.73)




Net ordinary income  
 $   95,268.91        48.92% of budget        ($193,613.69) 


     C.
Balance Report –2024



Rate Payer Checking:     $45195.57

Impact Fee Checking:     $ 17255.79


    
 LPID Rate Payer and Impact Fee checking accounts funds transfer authorization:  





Impact Fee Checking: $0.00      Rate Payer Checking   $0.00
5.
Operations Reports


A.
UPDES Compliance Report






May

June

July

Limits



Influent BOD   = 
207

113

170

ppm




Influent TSS     = 
169

338

201

ppm



Effluent BOD   =   
27

26

36

(limit is 45ppm).




Effluent TSS     =   
31

46

50

(limit is 45 ppm) 




pH    

  =       
8.6

8.7

8.9

(limit >6.0<9.0)




Coliform:   
  =        <1

1

<1

limit is 128)




Influent Flow    =     
0.643

0.511

0.352

mgd



Effluent Flow    =     
0.550

0.257

0.245

mgd



Effluent parameters were within permits except for effluent TSS at 50 mg/l. Aeration 



time is 4 hours/day for the month of July primarily for mixing in cell #1.  Cell #2 had a 



reduced algae bloom and Cell #3 was clear except for precipitated calcium carbonate. 



(White cloudiness, not green algae, see sample)



B.
Influent flow decreased from 0.511 mgd in May to 0.352 mgd in June. 
6.
Civic Review Process



Lake Point City has instigated a new check off list for entities to sign off on certain required 


documents before the city can issue a building permit.  LPID needs to develop a concise 




procedure for developers to follow to obtain a "Will Serve" notice and "Construction Plan" 


reviews. 


The District shall modify the "Utility Will Serve Notice" to include the language that the 
Lake 


Point Improvement District application for sewer service to be only a "Will Serve" notice and not 

an acceptance of construction plans for a building permit.  In addition to issuing the "Will Serve" 

notice, the District must also sign off on construction plans after being approved by the District 


engineer and the Board. 



AJ Shaffer shall provide a fee structure for reviewing all construction plans and to be approved 


by the 
Board. 
Such fees shall be charged to the Plan Review and Inspection fees collected at the 


time of the application of sewer service.
7.
Commercial Impact Fee Determination



The District Board has approved ERU calculation work sheet to calculate an impact fee for both 


residential and commercial users based on the water allocation from Oquirrh Mountain Water 


Company.  Water allocation of 0.45 to 1.00 acre-foot of water for residential indoor use only is 


equivalent to one (1) sewer ERU.    


The commercial allocation of sewer service shall be based on the calculated formula provided in 


a table in the District's "Standard Construction Manual" 
8.
Sewer Service Charges for Home Apartment Rentals


If an owner makes available any portion of a house, building or other properties for human 


habitation currently served by the District for the purpose of receiving payment or otherwise for 


compensation for occupancy, the owner, tenant or occupant shall be billed an additional sewer 


service fee for each unit sewer service is provided.

9.
Lake Point Road Repair




Lake Point City has not submitted any request for damage to roads caused by settlement of 


sewer trench failures. 


10.
Quick Sump Update



1.
Facility to be opened in July


2.
The volume of water to drain is estimated to be a maximum of 2 to 3 gallons per minute.



3.
A sample of the discharge water will be collected and analyzed for TSS, BOD, ammonia,




Phosphate and nitrate (awaiting enough flow to sample)


4.
The number of truckloads being delivered is now averaging about one per day.


11.
Franchise Agreement - Status


Update: No change
12.
Sewer Easement Update


The District Engineer is missing any easements for both Bridle walk and Davies Place
13.
Other District Business & Trustee Concerns


A. 
Next LPID Meeting—September 12, 2024


B.
Other Trustee business - None
 14.
Adjournment


Motion to adjourn this meeting of the Lake Point Improvement District of August 8, 2024 @ 8:49 pm        
Motion:  Todd;   Seconded: Ryan;   In Favor:   4;   Opposed:  0;   Motion Carries Yes
Minutes:  August
