Lake Point Improvement District

7856 Mountain View Road

Lake Point, Utah 84074

The Lake Point Improvement District held its regularly scheduled Business meeting on September 12, 2024 at 7:00 p.m. at the Broken Arrow Conference Room at 8960 Clinton Landing Road, Lake Point Utah.  The agenda is as follows:

1.
Call to Order


Chairman to call the meeting to come to order @:  7:05 pm

Motion:  Brady
Seconded:  Scott

Roll Call:
Todd   Brady   Scott   Jared   Ryan

Treasurer:  Terre Marshall
Engineer:  AJ Shaffer

Operator:  Keith Fryer    Guests:   None
2.
Public Concerns or Comments

  None

3.
Approval of Minutes


Business Meetings – August 2024


Comments or corrections:   None



Approval of the minutes for the Business Meetings of August 2024



Motion:  Scott;   Seconded:  Todd;   In Favor:  5;   Opposed:  0;   Carries:   Yes
4.
Financial Reports –


A.
Approval of Bills – 2024



Comments:  Terre reviewed each check draft for approval




Corrections/comments














ACH Merchant processing fee


$    30.55




Ward Engineering Services



$3405.00





Franchise & Business Law Group


$    50.00





Freedom Mailing




$   471.23




Electro Power (RPS VFD Repair)


$ 1551.00





Roto Rooter (Garrard sewer cleanup)


$ 1667.04




Utah Local Government Trust


$ 3832.39



     .
Motion to approve; Checks 44601 - 4611 + ACH fees $30.55;   Total: $16,068.61






        



    B.
Budget Report – 2024




Total Income

 $ 234,107.20
      73.1 % of budget        ($320,258.42)      



Total Expenses
 $   78,083.09        61.7 % of budget        ($126,644.73)




Net ordinary income  
 $ 156,024.11        80.6 % of budget         ($193,613.69) 


     C.
Balance Report –2024



Rate Payer Checking:     $37,948.83

Impact Fee Checking:     $17,255.79


     E.
LPID Rate Payer and Impact Fee checking accounts funds transfer authorization:



      No transfer: Waiting for billing from Lake Point City for road repair  





Impact Fee Checking: $ 0.00 

  Rate Payer Checking   $ 0.00
5.
Operations Reports


A.
UPDES Compliance Report






June

July

August
Limits



Influent BOD   = 
207

113

142

ppm




Influent TSS     = 
169

338

118

ppm



Effluent BOD   =   
27

26

16

(limit is 45ppm).




Effluent TSS     =   
31

46

39

(limit is 45 ppm) 




pH    

  =       
8.6

8.7

8.8

(limit >6.0<9.0)




Coliform:   
  =        <1

1

<1

limit is 128)




Influent Flow    =     
0.643

0.511

0.314

mgd



Effluent Flow    =     
0.550

0.257

0.232

mgd



Effluent parameters were within permits for effluent TSS at 39 mg/l. Aeration 




time is 4 hours/day for the month of August primarily for mixing in cell #1.  Cell #2 had a 


reduced algae bloom and Cell #3 was clear of precipitated calcium carbonate. 











B.
Influent flow decreased from 0.511 mgd in July to 0.314 mgd in August 
6.
Sewer Backup Invoice (Garrard)


Rooter Router has invoiced for the work to clean up the sewage back up in the Garrard home.



Should the District send the bill ($   ) to the insurance agency with the risk of paying the 



deductable and have the rate increase next renewal or pay the full amount 



File with the insurance Company (Utah local Government Trust)  



Motion 
     Seconded 
          In Favor         Opposed        Carries 





Pay the full amount out of sewer maintenance and repair?           


Motion:   Todd;    Seconded:  Scott;    In Favor:  5;   Opposed:   0;   Carries:   Yes


7.
Will Serve Notification


Language to be added to the Utility Will Serve Notice


      "The Lake Point Improvement District (LPID) by issuance of an approved application will 


        provide sewer service to the above mentioned property and is only a "Will Serve" notice, 


        NOT an acceptance of construction plans for a building permit.  Construction drawings and     

        specifications must be submitted to the Lake Point City Building Department and approved 


        by LPID Engineer through the building permit application process prior to issuance of a 


        building permit".
8.
LPID Approval of Construction Plans


Richmond American Homes (Mike Nash) in their home construction drawings do not provide 


plumbing drawings of the sub basement floor.  It is up to the plumber to lay out the piping and 


ultimately of location of the drain to the sewer lateral.  There is no set location of the drain to the 


sewer lateral; they are not always directly to the sewer lateral, but may be to the side, corner, and 

even back of the house.  It would be difficult architect to specify the elevation of the sewer drain


or the lateral or to have the plumbing contractor install footings to the exact elevation as may be


specified in the drawings. 


 In every case so far after 699 sewer lateral connections, the house drain has always been higher 


than the lateral. There is no practical way the plumbing contractor can measure the elevation of 


the sewer lateral / drain distance during installation.  (Most plumbing contractors do not have the 

equipment (laser levels) to accurately measure this distance)


Ward Engineering has 14 days to respond to the builder's construction drawing to verify or reject 

the drain/lateral elevations.  To date there have been some instances where the elevations were 


incorrect, i.e. the lateral elevation is higher than the drain elevation.  LPID will meet with the 


builder's construction engineering group to resolve the incorrect elevations.

9.
 Equipment Replacement


A. 
Spare Pump for $4 pump station.  Existing pumps are more than 30 years old.  


B.
Replacement of VFDs at Regional Pump Station.  VFDs are 23 years old.  Recent 




inspections of the VFDs are good, but ultimate life is unknown, installed in 2001


C.
Spare aeration units.  Life expectancy is unknown Installed in 2005
10.
Road Repair




Lake Point City indicated they would submit the road repair billing to the District for review


within the next two weeks.










11.
Quick Sump Update



1.
The volume of water to drain is estimated to be a maximum of 2 to 3 gallons per minute.



2.
The number of truckloads being delivered is now averaging about one per day.


3.
Water recovery system being investigated, no discharge




4.
Equipment to dewater car wash material is being investigated.  Solid to landfill, liquid to 



be recycled back to car wash facility
12.
Franchise Agreement - Status


Update   No change
13.
Sewer Easement Update


Ward Engineering has an updated map of the easements in the District
14.
Other District Business & Trustee Concerns


A. 
Next LPID Meeting—October 10, 2024 



B.
Other Trustee business:   None
 15.
Adjournment


Motion to adjourn this meeting of the Lake Point Improvement District on Sep12, 2024 @ 8:12 pm
Motion:  Brady;   Seconded:  Scott;   In Favor:  5;    Opposed:  0;   Motion Carries:    Yes
Minutes 8-24
