

          Lake Point Improvement District

7856 Mountain View Road

Lake Point, Utah 84074

APPROVED

Board Meeting Minutes

The Lake Point Improvement District held its regularly scheduled Business meeting on October 10, 2024 at 7:00 p.m. at the Broken Arrow Conference Room at 8960 Clinton Landing Road, Lake Point Utah.  The agenda is as follows:

1.
Call to Order 

Chairman to call the meeting to come to order @:  7:00 pm


Motion:   Brady

Seconded:  
Todd


Roll Call:
Todd   Brady   Jared;    Scott, Ryan Absent

Treasurer:  Terre Marshall


Operator:  Keith Fryer    Guests:  Jeff Caldwell; Levi Mele

2.
Public Concerns or Comments 

None                          

3.
Approval of Minutes 


Business Meetings – September 2024


Comments or corrections:   

None









Approval of the minutes for the Business Meetings of September 2024



Motion:  Brady;     Seconded:  Todd;     In Favor 3;   Opposed:    0;   Carries    Yes
4.
Financial Reports


A.
Approval of Bills – 2024



Comments:  Terre reviewed each check draft for approval




Corrections/comments:   None




ACH Merchant processing fee


$ 210.58




Ward Engineering   (Easement Documentation)
$8000.00    


     .
Motion to approve; Checks 4612 - 4618 + ACH fees $210.58;   Total: $13283.59









    Motion:  Jared;   Seconded:  Todd;   In Favor:  3; Opposed:  0; Motion Carries:  Yes:  

B.
Chartway Checking Accounts




Rate Payer 
$50,639.93
 



Impact Fee
$17,255.79


C.
Budget Report – 2023




Total Income

 $ 168296.18         52.6 % of budget        ($320,258.42)      



Total Expenses
 $   61983.93         44.3% of budget          ($126,644.73)




Net ordinary income  
 $   95,268.91        48.92% of budget        ($193,613.69) 


D.
Balance Report –2024



      Rate Payer Checking:  $1,341,217.28
Impact Fee Checking: $1,479,171.87

  
E.  
 LPID Rate Payer and Impact Fee checking accounts funds transfer authorization:  





Impact Fee Checking: $ 0.00

  Rate Payer Checking   $ 0.00
5.
Draft 2025 LPID Budget 


A.
A draft of the 2025 LPID budget was reviewed by the Trustees.


B.
Revisions:    Only minor revisions in thee income, expenses and equity income 




The changes will be made in the draft Budget hearing next Board meeting.



A motion to approve the Draft Budget for 2025





Motion:  Brady;     Seconded:  Todd;     In Favor:  3;   Opposed:    0;   Carries    Yes
6.
Operations Reports


A.
UPDES Compliance Report






June

July

September
Limits



Influent BOD   = 
113

170

221

ppm




Influent TSS     = 
338

201

235

ppm



Effluent BOD   =   
26

36

26

(limit is 45ppm).




Effluent TSS     =   
46

50

43

(limit is 45 ppm) 




pH    

  =       
8.7

8.9

8.9

(limit >6.0<9.0)




Coliform:   
  =        <1

<1

<1

limit is 128)




Influent Flow    =     
0.511

0.352

0.363

mgd



Effluent Flow    =     
0.257

0.245

0.234

mgd



Effluent parameters were within permits including the effluent TSS at 43 mg/l. Aeration 



time is 4 hours/day for the month of September primarily for mixing in cell #1.  Cell #2 



had a reduced algae bloom and Cell #3 was clear except for precipitated calcium 




carbonate. (White cloudiness, no green algae)



B.
Influent flow increased from 0.352 mgd in May to 0.363 mgd in September. 
7
NPDES Permit Renewal
.


Draft renewal of District's input of the new permit is ready for submittal to the Utah 



Division of Water Quality for review.  No new permitting parameters were submitted.




An explanation of the occasional TSS above current permits was noted.




Zero discharge incorporating the old salt ponds was introduced.
8.
Sewer Connection Application/Lateral Permit 


A.
Two documents were presented:




1.
Application for Sewer Connection



 
2.
Permit for Sewer Lateral


B.
Both documents were discussed by the Board



1.
The application for sewer service is the same as has been used in the past.  Some 




revisions may be warranted to bring it up to date.



2.
The permit for Sewer lateral needs no revision.
9.
Equipment Replacement


A.
The District has been advised to budget for replacement:

 



1.
VFD's at the regional pump station.




2.
Flow meter at the Regional Pump Station





3.
Standby pump for #4 Pump Station

10.
Lake Point Road Repair


A.
 Area submitted by Lake Point City




Colette and Shelby Road  






1964 Rock Hollow Road












1991 Rock Hollow Road




B.
Areas of concern?  Verify areas directly as a result of sewer trench failures.



The Lake Point Improvement District is only responsible for pipeline laying, manholes 



and service lateral into the lot property, not including backfill of the pipeline trenches.  






The Tooele County Road department had the responsibity to insure the road base were 



properly compacted and tested to insure it met road standards and Tooele County 




accepted the roads after the one year warranty expired.  Thus any failure of any part of the 


road should be the responsibility of Tooele County Road Department.  Lake Point 



Improvement District had no part of the trench backfill, testing or included in the 




warranty of the condition of the trench.  How can LPID be held responsible for any 



failures of the road that has occurred.


























C.
 Cost of repairs"









 Area submitted by Lake Point City?       Cost
  




Colette and Shelby Road  
  $16,198.20





1964 Rock Hollow Road
  $  3,234.00









1991 Rock Hollow Road
  $     442.00





1/3 Traffic / mobilization
  $     692.00







Total

  $22,130.60



Cost to be shared between the City and LPID:  40% City - 60% LPID

11.
Quick Sump Update


1.
The volume of water to drain is estimated to be less then 1 o 2gallons per minute.



2.
Most of the water is evaporated in the treatment process



3
The electrolytic process shows good chance of working to separate the water from the 



solids on a large scale.




4.
The plan is to decant the clear water from the treated cells into the grease trap holding 



tank (sealed off from discharging into the sewer) which would be trucked away to wash 



down car wash tanks.



5.
The number of truckloads being delivered is continues to be one per day.


12.
Franchise Agreement - Status


Update:  Nothing as of this date
13.
Sewer Easement Update


Update:  Ward Engineering will submit to the Board the area map of easements and a tabulated 


list of those completed and those in progress of being defined.
14.
Other District Business & Trustee Concerns


A. 
Next LPID Meeting—November 14, 2024



B.
The ULGT has had the LPID Website evaluated for being vulnerable software and 



hardware, encryption weakness, information leakage, and common mistakes and 




miss configurations were found to be at a "Low Level".


C.
Other Trustee business - None
 15.
Adjournment


Motion to adjourn this meeting of the Lake Point Improvement District of October 10, 2024 @ 8:45 pm      
Motion:  Brady;  Seconded:  Todd;  In Favor:   3;  Opposed:   0;  Motion Carries  Yes
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