Lake Point Improvement District

7856 North Mountain View Road

Lake Point, Utah 84744
APPROVED BOARD MEETING MINUTES MARCH 2025
The Lake Point Improvement District held its regular scheduled business meeting on March 13, 2025 beginning at 7:00 p.m. at the Broken Arrow Conference Room, 8960 Clinton Landing Road, Lake Point, Utah.  The agenda will be as follows:
1.
Call to Order 

Chairman to call the meeting to come to order @:  7:04

Motion:  Brady
Seconded:  Todd

Roll Call:
Todd   Brady   Jared (Absent)   Ryan (Absent)   Jeff


Treasurer:  Terre Marshall


Operator:  Keith Fryer   Engineer:  Brendan Thorpe   

  Guests:   Tim and Michelle Goldstein (Residents from Stansbury)
2.
Public Concerns or comments: Stansbury residents noted smell from water treatment across from 
Lake Point Auto Recycling and Canyon Road.  It is especially noticeable when traffic is stopped 
on SR36 and there is no other option to sit there and smell it.  There is little the district can 
eliminate this situation until the water temperature exceeds 50 degrees and the aerobic bacteria 
begin to become active eliminating the off gases producing smell.

3.
Approval of Minutes


Business Meetings – February 2025


Comments or corrections:   None


Approval of the minutes for the Business Meetings of February 2025

Motion: Todd;    Seconded:  Jeff;    In Favor 3;     Opposed:   0;     Carries:  Yes
4.
Financial Reports

A.
Approval of Bills – 2025


Comments:  Terre reviewed each check draft for approval



Corrections/comments:



ACH Merchant processing fee


$   58.11



Upper Case Printing




$ 121.60



Freedom Mailing




$ 518.37




Department of Environmental Quality

# 760.00




Voided Check





$     0.00



  Motion to approve; Checks 4855 - 4660, 4662 - 4663 + ACH fees $ 58.11;   Total: $5877.62 

   Motion: Brady;      Seconded:  Todd;      In Favor:   3;      Opposed:  0;    Motion Carries:  Yes   


B.
Chartway Checking Accounts



Rate Payer 
$53,287.29
 


Impact Fee
$17,255.79


C.
Budget Report – 2025


Total Income

 $   76,753.04       24.2 % of budget   ($317,215.25)     



Total Expenses
 $   14,008.87        10.2% of budget    ($ 15,967.00)



Net ordinary income  
 $   62,744.17       34.9% of budget     $179,870.25) 

D.
Balance Report –2025


 LPID Rate Payer & Impact Fee accounts funds transfer Authorization   



         Impact Fee Checking: $ 0.00;     Rate Payer Checking   $ 0.00
5.
Financial Records Storage.



The financial records that have been stored at the Big Canyon Well house are no longer 


available.  A total of 18 boxes of records were removed and taken to the Regional Pump 


Station building until a more permanent location can by found.

6.
Operational Reports



A.
 UPDES Compliance Report







December
January
February
Limits




Influent BOD

378

184

149

ppm





Influent TSS

177

172

141

ppm




Effluent BOD

21

14

20

(Limit 45 ppm)



Effluent TSS

44

20

26

(Limit 45 ppm)

  

pH


8.7

8.8

8.7

Limit >6.0 <9.0)


Coliform

<1

<1

<1

Limit 128)
`


Influent Flow

0.353

0.381

0.373

mgd




Effluent Flow

0.312

0.328

0.316

mgd


Effluent parameters were within permit limitations.  Aeration time increased to 12 

hours/day the first 12 days of February and was then increased to 22 hours per day 

the remaining of February.  Cell #2 has experienced a moderate reduction in algae 

bloom and cell #3 was clear


B.
Influent flow has decreased slightly in January from 0.384 mgd to 0.373 mgd in 


February.  Partial ice covers on lagoons only lasted about a week in mid February. 

C.
Lagoon status - winter turn over:  Only two odor complaints were received in 


February from residents out side Lake Point City while driving by on SR 36.
7.
UPDES Application Submittal

LPID received a letter dated February 7, 2025 indicating that the permit application to be 
complete.   The Division of Water Quality will now proceed to draft and issue the permit.  The 
draft permit will contain effluent ligations and other provisions reflecting the requirements of the 
State and Federal pollution control regulations.  The DEQ will then publish notice of the intent to 
issue the permit and allow thirty days for public comment.  A final permit will be issued sometime 
after the close of the public comment period.  A draft permit will be sent to LPID for review before 
the public notice.   
8.
Total Suspended Solids Violations - 001 Outfall


A warning letter was received in response to violations of UPDES Permit No. UT0020231 of 
pollutant concentrations higher than the allowable Permit limits for total suspended solids from 
March 2024 through July 2024.  The Act provides that any person who violates any permit, rule or 
order adopted under, it is subject to a civil penalty not to exceed $10,000 per day of such 
violation.


Be advised that future violations of this nature may be subject to formal enforcement action which 
may result in monetary penalties and/or other sanctions.
9.
Lagoon Odor Notification to Lake Point Business Center - Plat 2

The Lake Point Improvement District operates a facultative type waste water treatment system 
which on occasion, especially in the spring season, emits certain odors.  The odors may be 
annoying but are not harmful in any way.  There is little the treatment operation can be made until 
the water temperature is above freezing to allow the microbes to grow and consume the bacterial 
producing the odor.

Once the water temperature reached the critical point in what the microbes begin to grow and 
consume oxygen, then the aerators are operated to supply the necessary oxygen to keep the 
system aerobic.


"In the Declaration of Covenants, Conditions and Restrictions of Pastures at Saddleback P.U.D 
recorded August 4, 2015", as part of the Pastures at Saddleback Homeowners Association Rules 
and Bylaws, states that odor sources may exist from certain sources and home owners may be 
affected of such odor sources.  The same will apply to Lake Point Business Center Plat 2.
 Also to 
be included plats 1, 3, 4, & 5
10.
Proposed Lagoon Impoundment Area (Zero Discharge)


See charts


Chart #1 
Overview of LPID and SPID Lagoon area


Chart #2
Pipe line from LPID lagoons area east end Salt Plant impoundment area.


Chart #3
the ditch from Hardy Road to north section of salt plant


Chart #4
Present area of LPID containment east end of evaporation cells



Chart #5
Showing ditch from lagoons to Hardy Road (rb gate)


Chart #6
Chart showing ditch from Hardy Road / rb gate to east containment area



Chart #7
Chart showing Containment area


Chart #8
Close up of proposed containment area and inlet
11.
Claim No:  FSU5605 Constitution State; TPA: Utah Local Governmental Trust; LPID


1.
When was the district notified of the blockage?




The District was notified the day and hour the sewage backed up into the Garrard 



house.


2.
What actions were taken to address the blockage?



A Pipe View Jet cleaning was notified within an hour of the reported backup and 



the sewer main was cleaned within two hours the backup was detected.


3.
What was the blockage identified as?



The exact cause is unknown, but was suspected to be tree roots growing into the 



sewer main.



4.
Where was the blockage located?  On city property?




The blockage was believed to be located just east of the manhole on Foothill and 



Canyon Road. The sewer main was located in the Franchise property on Lake Point 


City.




5.
Have there been any history blockages in this line within the past 5 years?




No, there has been no history of blockages in this pipe line in the past 50 years.


6.
Has there been any other incidents to note related to this line?




No, no other incidents related in this pipeline since original pipe installation


7.
Is this line regularly maintained?  If so, what is done and are logs kept?




No, Manholes are inspected annually for backup and logs are kept.



8.
Photos?




Due to the location of the pipe into the sewer manhole, no photos were taken.


9.
Copy of PipeView Contractor service billing




A record of the Pipe-View service billing is available
12.
Blue Stake Member Services




As of this meeting, the Blue Stake notification procedure has not been set up.  The district 

is waiting for the GIS mapping to be completed.
13.
Other District Business or Trustee Concerns


A.
Next LPID Meeting - April 10, 2025

B.
Other Trustee Business

14.
Adjournment

Motion was made to adjourn the LPID Business meeting of March 13, 2025 @ 9:02 PM

Motion: Brady;      Seconded: Jeff;       In Favor:  3;    Opposed:   0; Motion Carries:   Yes

  

