2025 - Black

2024 – Light Blue     2023 – Purple

2022 – Red    2021 – Yellow

2020 – Blue   2019 – Green

April 2025

35%

40%

30%

30%

C

F

S

Water Department Information for April

- Our overall water consumption is lower compared to last month. It is lower than 2019 usage but slightly higher than the other past years.

- Aspen Grove wet-well levels are averaging 6.72 feet for April 2025 which is slightly higher than last month. Currently its sitting at 7.80 feet. This time last year, in April 2024, our average was 8.03 feet.

- Stewart Spring is averaging 64.43 gpm for April 2025, which is higher than last month. Currently it is coming int at 122 gpm. This time last year it was averaging 55 gpm for April 2024.

- Stewart spring overflow is running 0 gpm for the month of April which is down from last month. Total, Stewart Spring produced an average of 69.11 gpm for April.

- Unaccounted water

  - Upper Pressure Zone

    - Still at zero.

  - Lower Pressure Zone and Stewart Zone

    - Is lower than last month for the Lower pressure zone (Timphaven side) by 10%. The Stewart zone is about the same as last month. Hoping that once we fix that leak it will help with that zone as well.

- We have replaced 229 meters so far as of May 5th, 2024. And 211 meters are on cellular endpoints now.

- Aqua Engineering is working on the design of the Drinking water treatment facility.

- We have a CMGC out to bid for the water treatment facility.

- Aqua is working on master meters and updating the master plan.

- We fixed a leaking Hydrant on Children's Road. While fixing it we located 2 buried valves.

- We are working with the homeowners on Stewart Road to see if we can have them connect to the new high-pressure line and abandon the main line with a water leak.

- We have been working on a water conservation plan to submit to the State.

Wastewater Department Information for April

- We have one lab for April, all were within limits.

- One of two the EQ mixing pump went out and we have one on order for replacement. We are looking into other mixing options.

- Finalizing the asset document for the DEQ loan.

- Lift station cleaning was completed while Sundance was shut down.

- Constuction:

  - All non-essential supplies from the plant are now at Aline Storage.

  - They are getting close to having the excavation complete.

- Still getting pricing on:

  - HVAC system

  - Possible secondary sludge press

| AVERAGE DAILY FLOW (GPD) | 26,744 |
| --- | --- |
| HIGHEST DAILY FLOW (GPD) | 45,204 |