Lake Point Improvement District

7856 North Mountain View Road

Lake Point, Utah 84744
APPROVED APRIL 2025 MEETING MINUTES 

(APPROVED 09/11/2025)
The Lake Point Improvement District held its regular scheduled business meeting on April 10, 2025 beginning at 7:00 p.m. at the Broken Arrow Conference Room, 8960 Clinton Landing Road, Lake Point, Utah.  The agenda will be as follows:
1.
Call to Order 

Chairman to call the meeting to come to order @:  7:07 pm

Motion:  Brady
Seconded:  Ryan

Roll Call:
Todd   Brady   Jared   Ryan   Jeff


Treasurer:  Terre Marshall


Operator:  Keith Fryer   Engineer:  Brendan Thorpe   

Guests:  Levi Mele,   Kathleen VonHatten 
2.
Public Concerns or comments: Discussed lagoon intermittent odors 
3.
Approval of Minutes


Business Meetings – March 2025


Comments or corrections:   None


Approval of the minutes for the Business Meetings of March 2025

Motion: Brady;    Seconded:  Todd;     In Favor:  5;   Opposed:  0;    Carries:  Yes


4.
Financial Reports

A.
Approval of Bills – 2025


Comments:  Terre reviewed each check draft for approval



Corrections/comments:   None




ACH Merchant processing fee


$ 586.08



Ward Engineering




$610.9.50

  Motion to approve; Checks 4864 - 4673, + ACH fees $486.08;   Total: $12,332.89 

   Motion: Jeff;    Seconded:  Todd;     In Favor:   5;   Opposed:   0;    Motion Carries:   Yes;   


B.
Chartway Checking Accounts



Rate Payer 
$71,946.49
 


Impact Fee
$17,255.79

C.
Budget Report – 2025


Total Income

 $   80,237.93       28.4 % of budget   ($317,215.25)     



Total Expenses
 $   28,341.78       19.2 % of budget    ($ 15,967.00)



Net ordinary income  
 $   63,896.17       35.5 % of budget    ($179,870.25) 

D.
Balance Report –2025

       LPID Rate Payer & Impact Fee accounts funds transfer Authorization   



Impact Fee Checking: $0.00  
  Rate Payer Checking   $0.00 

5.
LPID Development Standards Manual



A.
This LPID Development Standards Manual was written as the District's  




Development Design Standards for new sewer infrastructure construction.


B.
Current fees are: $250 Plan Review and Inspection and Impact Fees $4131 per lot



For Example, 
Travel Lodge (20 ERU's), PR & I = $5000 and Impact Fees = 



$82,620.00.  Single Family:  PR&I = $250 and Impact Fee = $4131.00.


C.
Development Fee Schedule adopted by the current Board;   (Page 6)




Plan Review Single Family Residential Development
        $   450/lot




Plan Review Commercial Site Development


        $1,000/lot



Impact Fee per lot





        $4,131/lot


D
The Ward Engineer's review fee of each lot is set by the District at $300.00/lot.



E.
Once Ward Engineer's approval of the plan is made, the approval letter is forwarded 


to the Lake Point City's Recorder:




  Quote "We have reviewed the plot plan for the above-referenced 




project and have no further comments.  The plan is approved" 




F.
The City may issue a building permit based of the engineer's approval letter. 


G.
The District has paid Ward Engineering a total of $27,327.50 for all the lot reviews 


in 2024.  How does the District expect to recover these engineering costs?


H
Each of the three contractors presently used connecting sewer main to house laterals 


have made the in 2024 have not received any instructions, approvals or permits 



from Richmond American Homes or other building contractors regarding any 



approvals from LPID




I.
The Development and Standards Manual only applies to the subdivision sewer 



infrastructure.  Manholes placement and grade, Sewer cleanout details, Grease 



interceptor, Sewer Trench Backfill Detail, Grade and Alignment test, pipe slope 



Certificate Etc.


J.
This original Standards Manual calls for the developer/owner to obtain a "Permit 



for Service Lateral" from LPID prior to any service connection to a building (Page 


3 of Manual).   The developer (home builder) need only to obtained one permit 



from LPID for the entire Plat before connection begins.  (Not a new permit for each 


home)


K.
There have been 728 lateral connections in all the Saddleback Development without 




a single problem with any of the house to sewer main lateral connections
6.
Operational Reports



A.
 UPDES Compliance Report







January
February
March

Limits




Influent BOD

184

149

148

ppm





Influent TSS

172

141

98

ppm




Effluent BOD

14

20

27

(Limit 45 ppm)



Effluent TSS

20

26

36

(Limit 45 ppm)

  

pH


8.8

8.7

8.9

Limit >6.0 <9.0)


Coliform

<1

<1

<1

(Limit 128)
`


Influent Flow

0.381

0.373

0.434

mgd




Effluent Flow

0.328

0.316

0.329

mgd


Effluent parameters were within permit limitations.  Aeration time increased to 23 

hours/day.  Cell #2 has experienced a moderate reduction in algae bloom and cell 


#3 was nearly clear.

B.
Influent flow has increased in March from 0.372 mgd to 0.434 mgd.  

C.
Lagoon status -   Only two odor complaints were received in 




March from residents outside Lake Point City while driving by on SR 36.
7.
Review of draft UPDES 


Summary of Changes From Previous Permit


A.
Description of Discharge.  Outfall Number 001.  Unchanged from previous permit



B.
Receiving Waters and Stream Classification - Class 3E.  Severely habitat - limited




waters.  Narrative standards will be applied to protect these waters for aquatic 



wildlife.


C.
Total maximum Daily Load Requirements.  The receiving water is an unnamed 



ditch and downstream water bodies are not listed as impaired for any parameters 



according to 2024 303(d) list.



D.
Basis for Effluent Limitations




1.    Total Flow:  0.392 MGD:  New this permit, LPID shall appeal this limitation




2.    Total Residual Chlorine (TRC):  New this Permit 2.0 ppm.  OK



3.     Remaining limitations unchanged from previous permit.



E.
Self Monitoring and Reporting Requirements




The following self-monitoring requirements are the same as in the previous permit 


influent and effluent sample shall be composite sampling and except metal 



sampling was increased to semi-annual so as to gather data to run a 




reasonable potential analysis.  The permit will require reports to be submitted 



monthly and/or annually on DMR forms due 28 days after the end of the monitoring 


period.  Effective January 1, 2027, monitoring results must be submitted using 



NetDMR for bio-montoring , metals and toxic organics must be attached to the 



DMR's


8.
Lagoon Odor Notification to Lake Point Business Center - Plat 2


"In the Declaration of Covenants, Conditions and Restrictions of Pastures at Saddleback 


P.U.D 
recorded August 4, 2015", as part of the Pastures at Saddleback Homeowners 


Association Rules and Bylaws, states that odor sources may exist from certain sources 


and home owners may be affected of such odor sources.  The same will apply to Lake 


Point Business Center Plat 2.
 Also to be included plats 1, 3, 4, & 5.  Chris Robinson 


has included this language in the Declaration of Covenants Etc in all the Business 



Center Association and Bylaws.
9.
Proposed Lagoon Impoundment Area (Zero Discharge)



A.
Proposed area submitted to Chris Robinson


B.
Awaiting approval from DEQ


C.
Required improvements to salt ponds



D.
Time frame for completion of impoundment area

10.
Garrard Claim No:  FSU5605 


A.
Constitution State, Travelers Insurance Company


B.
TPA



C.
Utah Local Government Trust



D.
Communication to LPID
.


11.
Blue Stake Member Services



A.
Blue Stake Procedure



Procedure to be set up for LPID notification only




LPID General Manager to mark areas


B.
GIS Mapping Information

12.
Park Meadow Lane sewer drawings



The District will get final drawings from OMWC engineer.






13.
Other District Business or Trustee Concerns


A.
Next LPID Meeting - May 8, 2025

B.
Other Trustee Business

14.
Adjournment

Motion was made to adjourn the LPID Business meeting of April 10, 2025 @  09:49 pm


Motion: Brady;   Seconded:  Todd;    In Favor:  5;    Opposed:   0;      Motion Carries:     Yes  

