2025 - Black

2024 – Light Blue     2023 – Purple

2022 – Red    2021 – Yellow

2020 – Blue   2019 – Green

December 2025

C

F

S

Water Department Information for December

- Our overall water consumption is similar to last year.

- Aspen Grove wet-well levels are averaging 5.42 feet for December 2025 which is slightly down from last month. This time last year, in December 2024, our average was 5.86 feet.

- Stewart Spring is averaging 68 gpm for December 2025, which is same as last month. This time last year it was averaging 68 gpm for December 2024.

- Stewart spring overflow is running 2.35 gpm for the month of December which is down from last month. Total, Stewart Spring produced an average of 70.35 gpm for December 2025.

- Unaccounted water

  - Upper Pressure Zone

    - Still at zero.

  - Lower Pressure Zone and Stewart Zone

- COP has finished the roof on the water treatment plant. They are also doing electrical and inside construction. The filter canisters have been placed and piping should begin soon.

- Aqua is working on master meters and updating the master plan.

- We are now doing multiple water samples every other week. We are completing the PFAS sampling as well.

- We ordered two new master mag meters for the springs. Just waiting for them to arrive. Once they arrive, we will need to measure them and order new spools and valves.

- Unaccounted water elimination processes:

  - We have replaced almost all the service meters including the 6-inch meters.

  - Corrected meters with wrong calculations.

  - We have had the spring meters heartbeat checked multiple times

  - We have had 2 leak detection company's preform leak surveys

  - We have fixed multiple leaks

  - We have replaced 2 leaking hydrants.

  - We have inspected about 50 percent of the hydrants with a camera device.

  - We have had all the PRV’s inspected and replaced one 6 inch one 4 inch and two 2 inch PRV’s

  - We eliminated a section of old pipe on coming from the old Stewart Tank

  - We isolated Stewart tank to check for tank leaks.

  - We have two new zero meters ordered to replace the spring meters.

  - We started isolating zones in the system by transferring usage from stewart to Aspen grove sides.

Wastewater Department Information for December

- We have one lab for December; BOD was out of limits.

- The plant construction is moving forward they have plumbers and electricians in working.

- The blowers have been placed waiting on stainless steel piping.

- The mixing pumps have been installed.

- We are working through the process of keeping the plant operational and bringing new equipment online by the end of the month.

- We now have both MBR’s online.

- We had multiple sewer line sections camera inspected.

- We found a bad connection from the new Sundance maintenance sprung.

- We replaced all the rakes on the fine screen.

- We got the sewer system on the GIS map with GPS accuracy.

| AVERAGE DAILY FLOW (GPD) | 25,275 |
| --- | --- |
| HIGHEST DAILY FLOW (GPD) | 36,863 |