# 4.08.180 Cross Connection Control And Backflow Prevention

- Title And Purpose. This Section shall be known as the “Culinary Water Source Protection and Backflow Prevention Ordinance.”The purpose of the ordinance is to ensure the provision of a safe and sanitary drinking water supply for the City by the establishment of culinary backflow prevention definitions and requirements to protect the health and safety of those using the water system.

- Definitions. When used in this Section, the following words and phrases shall have the following meanings:

APPROVED BACKFLOW ASSEMBLY. An assembly accepted by the Utah State Department of Environmental Quality, Division of Drinking Water meeting an applicable specification or as suitable for the proposed use.

AUXILIARY WATER SUPPLY. Any water supply on or available to the premises other than the city's public water supply will be considered as an auxiliary water supply. These auxiliary waters may include water from another city's public potable water supply or any natural source(s) such as a well, spring, river, stream, harbor, etc., or "used waters" or "industrial fluids". These waters may be contaminated or polluted or may be objectionable and constitute an unacceptable water source over which the Water Superintendent does not have authority for sanitary control.

BACKFLOW. The reversal of the normal flow of water caused by either back-pressure or back-siphonage.

BACK-PRESSURE. The flow of water or other liquids, mixtures, or substances under pressure into the feeding distribution pipes of a potable water supply system from any source(s) other than the intended source.

BACK-SIPHONAGE. The flow of water or other liquids, mixtures, or substances into the distribution pipes of a potable water supply system from any source(s) other than the intended source, caused by the reduction of pressure in the potable water supply system.

BACKFLOW PREVENTION ASSEMBLY. An assembly or means designed to prevent backflow. Specifications for backflow prevention assemblies are contained within the Plumbing Code, as adopted by the State of Utah in the Cross Connection Control Program for Utah maintained by the Division of Drinking Water.

CONTAMINATION. Degradation of the quality of the potable water supply by sewage, industrial fluids or waste liquids, compounds, or other materials that

may create a health hazard.

CROSS CONNECTION. Any physical connection or arrangement of piping or fixtures that may allow non-potable water or industrial fluids or other material of questionable quality to come in contact with potable water inside a distribution system. This would include any temporary conditions, such as swing connections, removable sections, four-way plug valves, spools, dummy sections of pipe, swivel or change-over devices, sliding multiport tubes, or other plumbing arrangements.

CROSS CONNECTION-CONTROLLED. A connection between a potable water system and a non-potable water system with an approved backflow prevention assembly properly installed and maintained so that it will continuously afford the protection commensurate with the degree of hazard.

CROSS CONNECTION-CONTAINMENT. The installation of an approved backflow assembly as the water service connection to any premises where it is physically and economically infeasible to find and permanently eliminate or control all actual or potential cross connections within the water distribution system; or, it shall mean the installation of an approved backflow prevention assembly on the service line leading to and supplying a portion of a water system when there are actual or potential cross connections that cannot be effectively eliminated or controlled at the point of the cross connection (isolation).

RIGHT OF ENTRY. Employees of the City shall have the right to enter any place which is plumbed with water from the City drinking water distribution system to conduct a hazard survey or any other examination or test reasonably required for the enforcement of this Section.

RESPONSIBILITY OF COST. Any user of drinking water installing a backflow prevention device or assembly shall pay all costs for installation and testing.

TESTING. Backflow prevention devices must be tested by the owner 10 days after installation and every year thereafter by a technician certified by the Utah State Division of Drinking Water. Test results shall be furnished to the Public Works Department of the City and the Utah State Division of Drinking Water.

VIOLATION. Drinking water service may be discontinued to any user who is found in violation of this Section and who fails to take corrective action within ten days after violation notification, except that drinking water service may be discontinued immediately if a threat to the water supply exists. person who violates the provisions of this Section shall be civilly liable to Payson City, or to third persons suffering damage, for all damages approximately caused by said violation.

PRESSURIZED IRRIGATION CROSS CONNECTION. Pressurized irrigation water is not treated and is not to be used for any drinking water purpose, but is for outdoor watering use only. There shall be no direct connection between Culinary and Pressurized Irrigation lines. In addition to any criminal penalty, such person violating this requirement shall be subject to termination of drinking and pressurized irrigation water service from the City and shall be responsible for the costs of disinfecting the City’s drinking water system, together with all other costs incurred by the City as a result of the cross connection.

# Requirements.

  - No water service connection to any premises shall be installed or maintained by the Water Superintendent unless the water supply is protected as required by State laws, regulations, codes, and this ordinance. Service of water to a lot, parcel, or property found to be in violation of this ordinance shall be discontinued by the Water Superintendent after due process of written notification of violation and an appropriate time suspense for voluntary compliance, if:

  - A backflow prevention assembly required by this ordinance for the control of backflow and cross connections is not installed, tested, and maintained, or

  - It is found that a backflow prevention assembly has been removed or by-passed, or

  - An unprotected cross connection exists on the premises, or

  - The periodic system survey has not been conducted.

- Service will not be restored until such conditions or defects are corrected.

- The system(s) shall be open for inspection at all reasonable times to authorized representatives of the Water Superintendent to determine whether cross connections or other structural or sanitary hazards, including violation of this ordinance exist and to audit the results of the required survey (R309-105-12 of the Utah Administrative Code).

- Whenever the Water Superintendent deems a service connection’s water usage contributes a sufficient hazard to the water supply, an approved backflow prevention assembly shall be installed on the service line of the identified consumer’s water system, at or near the property line or immediately inside the building being served; but, in all cases, before the first branch line leading off the service line.

- The type of protective assembly required shall depend upon the degree of hazard that exists at the point of cross connection (whether direct or indirect), applicable to local and state requirements or resulting from the required survey.

- All presently installed backflow prevention assemblies that do not meet the requirements of this Section but were approved assemblies for the purposes described herein at the time of installation and that have been properly maintained, shall, except for the inspection and maintenance requirements, be excluded from the requirements of these rules so long as the Water Superintendent is assured that it will satisfactorily protect the public water system.

- Whenever the existing backflow preventer is moved from the present location or requires more than minimum maintenance or when the Water Superintendent finds that the operation of this assembly constitutes a hazard to health, the unit shall be replaced by an approved backflow prevention assembly meeting all local and state requirements.

- It shall be the responsibility of the consumer at any premises where backflow prevention assemblies are installed to have certified survey/inspections, and operational tests made at once per year at the consumer’s expense. In those instances where the Water Superintendent deems the hazard to be great, certified surveys/inspections and tests may be required at more frequent intervals. It shall be the duty of the Water Superintendent to see that these tests are made according to the standards set forth by the State Department of Environmental Quality, Division of Drinking Water.

- All backflow prevention assemblies shall be tested within ten (10) working days of initial installation.

- No backflow prevention assemblies shall be installed so as to create a safety hazard. Example: Installed over an electrical panel, steam pipes, boilers, or above ceiling level.

# Pollution Of Culinary Water System.

- Protection of culinary water from the possibility of contamination or pollution through compliance with Utah Public Drinking Water Rules (UPDWR) and the Plumbing Code, as adopted by the State of Utah. Compliance with these minimum safety codes will be considered reasonable vigilance for prevention of contaminants or pollutants that could backflow into the public culinary water system.

- It shall be unlawful at any place supplied with water from the city culinary water system:

- To install or use any physical connection or arrangement of piping or fixtures that may allow any fluid or substance not suitable for human consumption to come in contact with potable water in the city culinary water system.

- To connect the culinary water system and pressurized irrigation water system together.

- To install any connection, arrangement, or fixtures without using a backflow prevention device or assembly designed to prevent backflow. Any such device or assembly must be approved for installation by the City Engineer.

- To install any backflow prevention device or assembly that is not installed as required in the adopted Plumbing Code.

Any user of the city culinary water system shall pay all costs of installation and testing of backflow prevention devices or assemblies. Backflow prevention devices or assemblies required by this Section shall be tested as frequently as determined by the City Engineer. Test results shall be furnished to the City and the Utah State Department of Environmental Quality, Division of Drinking Water.  Backflow prevention assemblies required by this section shall be tested at the time of installation or within 10 days of being placed into service, immediately after repairs or relocation and at least annually. Test results shall be submitted to the City water Cross-Connection Control Program Administrator or their agent.

Water service may be discontinued to any user who is found to be in violation of this Section and who fails to take corrective action within ten (10) days after notification, except that water service may be disconnected immediately if an immediate threat to the water supply exists. Any person who violates the provisions of this Section shall be liable to the City, and third parties other than the City, for all damage caused by the violation.

The responsibility to enforce the applicable sections of the Plumbing Code begins at the point of service (downstream side of the meter) and continues throughout the developed length of the city culinary water system. The City Engineer or designee will review all plans to ensure that unprotected cross connections are not an integral part of the water system. If a cross connection cannot be eliminated, it must be protected by the installation of an air gap or an approved backflow prevention assembly, in accordance with the adopted Plumbing Code. Water vacating the culinary water system must do so via an approved air gap or approved mechanical backflow prevention assembly, properly installed and in accordance with the adopted Plumbing Code.

Whether employed by the consumer or utility to survey, test, repair, or maintain backflow prevention assemblies the certified backflow technicians, surveyors, or repair persons will have the following responsibilities:

To insure acceptable testing equipment and procedures are used for testing, repairing, or overhauling backflow prevention assemblies.

To make reports of testing and/or repair to the Water Superintendent on a form approved for such use by the Water Superintendent within time frames as described by the Division of Drinking Water.

Prepare a report that shall include the list of materials or replacement parts used. Replacement parts shall be equal in quality to parts originally supplied by the manufacturer of the assembly being repaired. A certified technician shall perform all tests of the mechanical assemblies and be responsible for the competence and accuracy of all tests and reports.

To not change the design, material, or operational characteristics of the assembly during testing, repair, or maintenance.

To insure the license is current, the testing equipment being used is acceptable to the State of Utah, and is in proper operating condition and to be equipped with, and be competent to use, all necessary tools, gauges, and other equipment necessary to properly test, and maintain backflow prevention assemblies.

The certified technician conducting the test must tag each double check valve, pressure vacuum breaker, reduced pressure backflow assembly and high hazard air gap, showing the serial number, date tested, and by whom. The technician's license number must also be on this tag. In the case of a consumer requiring an assembly to be tested, any certified technician is authorized to make the test and report the results of that test to the consumer, and the Water Superintendent. The installation, replacement, or repair of assemblies must be made by a tester having appropriate licensure from the Department of Commerce, Division of Professional Licensing, except when the backflow technician is an agent of the assembly owner.

HISTORY

Adopted by Ord. 05-18-2022-D on 5/18/2022 Amended by Ord. 09-07-2022-A on 9/7/2022