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Unaccounted water went from 30% last month to 23.88%
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Water Department Information for July 
· Our overall water consumption is lower than in the last two years. 
· Aspen Grove wet-well levels are averaging 7.6 feet for July 2026 which is the same as last month. This time last year, in July 2025, our average was 8 feet. 
· Stewart Spring is averaging 85 gpm for July 2026, which is up from last month. This time last year it was averaging 115 gpm for July 2025. 
· Stewart spring overflow is running 20 gpm for the month of July which is down from last month. Total Stewart Spring produced an average of 105 gpm for July 2026. 
· Construction is almost complete at the treatment plant 
· Power conduit is installed. Waiting on RMP to pull and energize the line. 
· They are painting the pipes inside.
· We still need to have additional equipment installed. 
· We repaired the leak we found on Stewart Road. There were two separate leaks next to each other. 
· We have had 86 submit lead and copper surveys up from 15 last month.				
· Unaccounted water elimination processes:
· We have replaced almost all the service meters including the 6-inch meters. 
· Corrected meters with wrong calculations, and mismatched register sizes. 
· We have had the spring meters heartbeat checked multiple times
· We have had 2 leak detection companies conduct leak surveys 
· We have fixed multiple leaks 
· We have replaced 2 leaking hydrants.
· We have inspected about 50 percent of the hydrants with a camera device. 
· We have had all the PRV’s inspected and replaced one 6 inch one 4 inch and two 2 inch PRV’s
· We eliminated a section of old pipes on coming from the old Stewart Tank
· We isolated Stewart tank to check for tank leaks. 
· We have two new zero meters ordered to replace the spring meters. 
· We started isolating zones in the system by transferring usage from Stewart to Aspen grove sides.
· Leak locators came back out.
· Dug and fixed a leak on stewart rd.
· Replaced both spring meters. 
· Fixed a double leak on stewart rd. 












Wastewater Department Information for July 
· We completed one lab test in July, and all results were within limits. FOG was reported as not detected; because the lab cannot measure below 5 mg/L, the result is below the detectable limit.
· MBR tank 3 is online and running.
· MBR 1 and 2 have the new Kabota membranes installed.
· They will be working on installing new piping and pumps. 
· Sundance is planning to repair our electrical lines that were hit on the upper drain field. 
· Update they have put a new conduit in now we just need the line put in and wired up.  
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	AVERAGE DAILY FLOW (GPD)
	27,425

	HIGHEST DAILY FLOW (GPD)
	38.530
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Wastewater Labs Chart 2026

BOD LBS	
Limits 	June 29th	July 28th	72	55.44	20.03	TSS LBS	
Limits 	June 29th	July 28th	72	53.89	24.57	FOG LBS	
Limits 	June 29th	July 28th	14	2.87	0	



Source Total: 12,070,186 Gallons

Source Total: 4,747,376 Gallons	


District Metered Usage 	Conveyed Water Usage	Unaccounted Stewart Zone	Unaccounted Lower Pressure zone	Unaccounted Upper Pressure Zone	4471816	4735135	1493351	1389350	0	
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